# Latency Budget and Re-timed Simulation Results

TABLE I

End-to-End Latency Budget of the CNN-LSTM Control Chain

| Stage | Time |
| --- | --- |
| PMU observation window | 500 ms |
| Preprocessing | 1.9 ms |
| CNN-LSTM inference (CPU, mean) | 17.3 ms |
| Decision available after onset | 519.2 ms |
| Communication delay (Tcomm) | 0–500 ms (examined) |
| STATCOM response time | < 30 ms |
| SVC response time | ≈ 150 ms |
| Total to STATCOM corrective action | ≈ 549 ms + Tcomm |
| Total to SVC corrective action | ≈ 669 ms + Tcomm |

TABLE II

Event and Corrective-Action Instants Used in Each Figure

| Figure | Device | Disturbance (s) | Decision (s) | Action, Tcomm=0 (s) | Action, Tcomm=200 ms (s) |
| --- | --- | --- | --- | --- | --- |
| Rotor angle, G1/G4/G7/G10 | STATCOM | 0.10 | 0.619 | 0.649 | 0.849 |
| Rotor angle, G1/G4/G7/G10 | SVC | 0.10 | 0.619 | 0.769 | — |
| System frequency | SVC | 0.50 | 1.019 | 1.169 | 1.369 |
| Two-panel Δδ (G10) | STATCOM | 0.10 | 0.619 | 0.649 | 0.849 |
| Two-panel Δδ (G10) | SVC | 0.10 | 0.619 | 0.769 | — |
| Bus 44 voltage (wind variability) | SVC | 0.50 | 1.019 | 1.169 | 1.369 |
| Bus 44 voltage collapse | SVC | 0.50 | 1.019 | 1.169 | 1.369 |
| Frequency deviation (9/39/118-bus) | SVC | 0.50 | 1.019 | 1.169 | — |
| G10 NC / CC / PF | STATCOM | 0.10 | 0.619 | 0.649 | 0.849 |
| G10 delay sensitivity | STATCOM | 0.10 | 0.619 | 0.649 | 0.649 + Tcomm |
| STATCOM saturation | STATCOM | 0.25 | 0.769 | 0.799 | — |

Action instant = disturbance + 519.2 ms + device response (30 ms STATCOM, 150 ms SVC) + Tcomm.

TABLE III

Key Results of the Re-timed Figures

| Figure | Case | Metric | Value |
| --- | --- | --- | --- |
| Rotor angle (G10) | No control | Peak δ | Loses synchronism |
|  | STATCOM, Tcomm=0 | Peak δ | 52.9° |
|  | STATCOM, Tcomm=200 ms | Peak δ | 117.4° |
|  | SVC, Tcomm=0 | Peak δ | 97.1° |
| System frequency | No control | Nadir | 48.30 Hz |
|  | Conventional PI-AGC | Nadir | 49.10 Hz |
|  | CNN-LSTM + SVC, Tcomm=0 / 200 ms | Nadir | 48.30 Hz (before action) |
| Two-panel Δδ (G10) | STATCOM, Tcomm=0 | Peak Δδ | 20.7° |
|  | STATCOM, Tcomm=200 ms | Peak Δδ | 43.1° |
|  | SVC, Tcomm=0 | Peak Δδ | 34.6° |
| Bus 44 voltage (wind variability) | SG-only baseline | Nadir / time < 0.90 p.u. | 0.889 p.u. / 1.0 s |
|  | 50% RES, no control | Nadir / time < 0.90 p.u. | 0.831 p.u. / 4.2 s |
|  | CNN-LSTM + SVC, Tcomm=0 | Nadir / time < 0.90 p.u. | 0.859 p.u. / 1.4 s |
|  | CNN-LSTM + SVC, Tcomm=200 ms | Nadir / time < 0.90 p.u. | 0.843 p.u. / 1.4 s |
| Bus 44 voltage collapse | NC | Final state | Collapse < 0.60 p.u. |
|  | CC | Nadir / final | 0.785 / 0.86 p.u. |
|  | PF, Tcomm=0 | Nadir / time < 0.90 p.u. | 0.858 p.u. / 1.0 s |
|  | PF, Tcomm=200 ms | Nadir / time < 0.90 p.u. | 0.827 p.u. / 1.5 s |
| Frequency deviation (a), 39-bus | No control / PI-AGC | Δf nadir | −1.70 / −0.90 Hz |
|  | CNN-LSTM + SVC | Δf nadir | −1.70 Hz (before action) |
| Frequency deviation (b) | 9 / 39 / 118-bus, CNN-LSTM + SVC | Δf nadir | −0.57 / −0.67 / −0.75 Hz |
|  | 9 / 39 / 118-bus, second dip | No control → CNN-LSTM | −0.27/−0.31/−0.35 → ≈ −0.04 Hz |
| G10 NC / CC / PF | NC | Loss of synchronism | 1.44 s |
|  | CC | Loss of synchronism | 1.68 s |
|  | PF, Tcomm=0 | Peak δ | 51.6° |
|  | PF, Tcomm=200 ms | Peak δ | 79.5° |
| STATCOM saturation | Case T alone (140 Mvar) | Peak δ / margin | 64.9° / 115° |
|  | Combined (205 Mvar demand, capped 150) | Peak δ / margin | 81.2° / 99° |
|  | Combined | Saturation window | 0.809–1.59 s |
|  | No control | 180° crossing | 1.70 s |

TABLE IV

Communication-Delay Sensitivity of G10 Transient Stability

| Tcomm (ms) | STATCOM action (s) | STATCOM peak δ | SVC action (s) | SVC peak δ |
| --- | --- | --- | --- | --- |
| 0 | 0.649 | 52.9° (stable) | 0.769 | 97.1° (stable) |
| 50 | 0.699 | 66.2° (stable) | 0.819 | 116.4° (stable) |
| 100 | 0.749 | 81.8° (stable) | 0.869 | 136.2° (stable) |
| 150 | 0.799 | 99.3° (stable) | 0.919 | 156.1° (stable) |
| 200 | 0.849 | 117.4° (stable) | 0.969 | Unstable |
| 250 | 0.899 | 135.3° (stable) | 1.019 | Unstable |
| 300 | 0.949 | 152.0° (stable) | 1.069 | Unstable |
| 350 | 0.999 | Unstable | 1.119 | Unstable |
| 400–500 | 1.049–1.149 | Unstable | 1.169–1.269 | Unstable |

Critical Tcomm ≈ 342 ms for STATCOM (≈ 891 ms total after fault onset) and ≈ 150–200 ms for SVC.